## PMV-PPD direct
Model for the calculation of thermal comfort indices PMV and PPD (ISO 7730 - Fanger's method)
| Input Data |  |  | Intermediate Calculations | [6 empty] | Output Data
| M (met) = | 3
| W (met) = | 0 |  | T skin = | 30.8154 | ºC
| I cl (clo) = | 0.4
| Ta (ºC) = | 18 |  | hc natural conv = | 3.9624
| Tr (ºC) = | 17 |  |  |  | max hc = | 5.4113 | (W/m2 ºC)
| pa (Pascal) = | 1400 |  | hc forced conv = | 5.4113
| Va (m/s) = | 0.2
[7 empty] | Tcl = |  | 25.6827 | ºC
| M (W/m2) = | 174.45 |  | fcl (Icl<0.5 clo) = | 1.08
| W (W/m2) = | 0 |  |  |  | min fcl = | 1.08 | (m2 ºC/W)
| Icl (m2 ºC/W) = | 0.062 |  | fcl (Icl>0.5 clo) = | 1.09 |  |  | Coeficiente | 0.028568 |  | PMV = | 0.46187
| Tcl inicial = | 25.6828 |  |  |  |  | Heat Fluxes | perspiration | 9.4965 | (W/m2)
| Control of Iterative Method |  | ºC |  |  |  |  | sweating | 48.846 | (W/m2)
| (Tcl-Tclini) = | -0.00011861
|  |  | ºC |  |  |  |  | breathing (latent) | 13.2476 | (W/m2)
| Enable Macros After introducing data, Press Run Button. After calculation, (Tcl - Tclini) must be equal to 0. | [9 empty] | PPD (%) = | 9.4532
[8 empty] | breathing (sensible) | 3.9077 | (W/m2)
[8 empty] | radiation | 37.8862 | (W/m2)
[8 empty] | convection | 44.8984 | (W/m2)
[8 empty] | Total Flux (Q) | 158.2823 | (W/m2)
©Manuel Gameiro da Silva, DEM-FCTUC manuel.gameiro@dem.uc.pt
[8 empty] | Balance [(M-W) - Q] | 16.1677 | (W/m2)
|  | W/m2 |  | %
| (M-W) | 174.45
| Q | 158.2823
| convection | 44.8984 |  | 28.366
| radiation | 37.8862 |  | 23.9358
| sweating | 48.846 |  | 30.8601
| perspiration | 9.4965 |  | 5.9997
| breathing (latent) | 13.2476 |  | 8.3696
| breathing (sensible) | 3.9077 |  | 2.4688
o
o

## PMV data Tar, HR, Tmr, Var
Model for the calculation of PMV and PPD (ISO 7730 - Fanger's Method) - Data of Temp/Humidity/Mean Rad Temp/Air Vel
| Input Data |  | Intermediate Calculations | [6 empty] | Output Data
| M (met) = | 1.2
| W (met) = | 0 | T skin = | 33.7462 | ºC
| I cl (clo) = | 0.5
|  |  | hc natural conv = | 3.8652
| Ta (ºC) = | 22 |  |  | max hc = | 3.8652 | (W/m2 ºC)
| HR (%) = | 60 | hc forced conv = | 3.8264
| Tmr (ºC) = | 22
| Var (m/s) = | 0.1 |  |  |  | Tcl = |  | 28.9561 | ºC
| M (W/m2) = | 69.78 | fcl (Icl<0.5 clo) = | 1.1
| W (W/m2) = | 0 |  |  | min fcl = | 1.1 | (m2 ºC/W) |  |  | PMV = | -0.75305
| Icl (m2 ºC/W) = | 0.0775 | fcl (Icl>0.5 clo) = | 1.1 |  |  | Coeficiente | 0.052573
| Tcl ini = | 28.9561
[6 empty] | Heat Fluxes | perspiration | 11.1611 | (W/m2)
|  |  | Temp. Med. Rad. = | 22 | ºC |  | sweating | 4.8846 | (W/m2)
| Control of Iterative Method |  | Vapour Pressure = | 1585.8626 | Pa |  | breathing (latent) | 5.0785 | (W/m2)
| (Tcl-Tcl ini) = | 2.6707e-05
[7 empty] | breathing (sensible) | 1.1723 | (W/m2) | PPD (%) = | 16.9431
[7 empty] | radiation | 32.233 | (W/m2)
|  |  | A = | 0.00070554
|  |  | Pvs(Tdb) = | 2.6431 |  |  | convection | 29.5744 | (W/m2)
[6 empty] | Total Flux (Q) |  | 84.1039 | (W/m2)
©Manuel Gameiro da Silva, DEM-FCTUC manuel.gameiro@dem.uc.pt
|  |  | Pv = | 1.5859 |  | Balance [(M-W) - Q] |  | -14.3239 | (W/m2)
|  | W/m2 | %
| (M-W) | 69.78
| Q | 84.1039
| convection | 29.5744 | 35.1641
| radiation | 32.233 | 38.3252
| sweating | 4.8846 | 5.8078
| perspiration | 11.1611 | 13.2706
| breathing (latent) | 5.0785 | 6.0384
| breathing (sensible) | 1.1723 | 1.3939